## Working Sheet - ALL PRODUCTS
| SuperLite I | SuperLite I-XL | SuperLite I-W | SuperLite X-45/60/90 | SuperLite II-XL 45 | SuperLite II-XL 60 | SuperLite II-XL 90 | SuperLite II-XL 120 | Pyran Platinum | Pyran Platinum F | Pyran Platinum L | Fireglass 20 | Pyrodur | WireLite NT | FireLite | FireLite NT | FireLite Plus | Pyrostop 45 | Pyrostop 60 | Pyrostop 90 | Pyrostop 120 | Pyroswiss | Keralite Standard R (FR-R) | Keralite Standard F (FR-F) | Keralite Standard L (FR-L) | Keralite Select F | Keralite Select L | Keralite Ultra | Contraflam 45 (Swissflam) | Contraflam 60 | Contraflam 90 | Contraflam 120 | PyroEdge 20 | Pyrobel 45 | Pyrobel 60 | Pyrobel 90 | Pyrobel 120
Fire Rating | 20 min | 20 min - 60 min | 20 min - 90 min | 45 min - 90 min | 45 min | 60 min | 90 min | 120 min | 20 min - 90 min | 20 min - 3 hours | 20 min - 3 hours | 20 min | 20 min | 20 min - 90 min | 20 min - 90 min | 20 min - 3 hours | 20 min - 3 hours | 45 min | 60 min | 90 min | 120 min | 20 min | 45 min - 90 min | 45 min - 3 hours | 45 min - 3 hours | 20 min - 3 hours | 20 min - 3 hours | 45 min - 3 hours | 45 min | 60 min | 90 min | 120 min | 20 min | 45 min | 60 min | 90 min | 120 min
Origin for Glazing | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Imported | Imported | Imported | Manufactured in the USA | Imported | Unknown | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported |  |  | USA | Manufactured in the USA | Imported | Imported | Imported | Imported
Glass Make-up | Clear Tempered. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Specialty Tempered | Safety Filmed Wired Glass | Specialty Glass | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Ceramic | Filmed Ceramic | Laminated Ceramic | Tempered | Annealed | Safety Filmed Wired Glass | Ceramic | Filmed Ceramic | Laminated Ceramic | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Tempered | Ceramic | Filmed Ceramic | Laminated Ceramic | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic | Annealed |  |  | Tempered | Tempered | Annealed | Annealed | Annealed | Annealed
Visual Appearance | Clear | Clear | Clear with Wire | Clear | Clear | Clear | Clear | Clear | Neutral. No polishing required, with savings passed to customer. | Neutral. No polishing required, with savings passed to customer. | Neutral. No polishing required, with savings passed to customer. | Clear | Clear | Clear with Wire | Amber Tint. Polishing required for premium-priced version. | Amber Tint. Polishing required for premium-priced version. | Amber Tint. Polishing required for premium-priced version. | Clear | Clear | Clear | Clear | Clear | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Clear | Clear | Clear | Clear | Clear | Clear | Clear | Clear | Clear
Light Transmission | Approx. 89.5% | Approx. 81% | Approx. 86% | Approx. 81% | Approx. 85-90% | Approx. 85-90% | Approx. 81-89% | Approx. 81-89% | Unknown | Unknown | Unknown | Approx. 89% | Approx. 78% | Approx. 77% | Approx. 88% | Approx. 88% | Approx. 85% | Approx. 86% | Approx. 87% | Approx. 84% | Approx. 74-75% | Approx. 89% | Approx. 88% | Approx. 88% | Approx. 82% | Approx. 88% | Approx. 82% | Approx. 79% | Approx. 84% | Approx. 85% | Approx. 82% | Approx. 82% | Approx. 87-89% | Approx. 85% | Approx. 81% | Approx. 82% | Approx. 71%
ASTM E-119 Heat Barrier | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes
Impact Safety Rating | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | Not safety rated | CSPC Cat. I & II | CSPC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I only | CPSC Cat. I & II | Not safety rated | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | Not safety rated | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
Hose Stream | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes
Acoustical Barrier | Approx. STC 28 | Approx. STC 28 | Approx. STC 28 | Approx. STC 38 | Approx. STC 40 | Approx. STC 42 | Approx. STC 44 | Approx. STC 44 | Approx. STC 35 | Approx. STC 35 | Approx. STC 36 | No | No | No | Approx. STC 35 | Approx. STC 35 | Approx. STC 38 | Approx. STC 40 | Approx. STC 41 | Approx. STC 45 | Approx. STC 46 | Approx. STC 32 | Approx. STC 35 | Approx. STC 35 | Approx. STC 37 | Approx. STC 35 | Approx. STC 37 | Approx. STC 38 | Approx. STC 39 | Approx. STC 40 | Approx. STC 45 | Approx. STC 46 | No | Approx. STC 39 | Approx. STC 42 | Approx. STC 43 | Approx. STC 46
Thickness/Weight per sq. ft. 20 min | 1/4" / 3.0 lbs | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | [5 empty] | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | 1/4" / 3.0 lbs | 5/16" / 3.48 lbs | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs |  |  |  |  | 1/4" / 3.2 lbs |  |  |  | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | [5 empty] | 1/4" / 3.0 lbs or 3/8" / 4.5 lbs
Thickness/Weight per sq. ft. 45 min |  | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs | 3/4" / 8.0 lbs standard (1/2" thin profile also available) |  |  |  | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs |  |  | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | 3/4" / 9.2 lbs |  |  |  |  | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | 3/4" / 8.0 lbs |  |  |  |  | 5/8" / 8.2 lbs
Thickness/Weight per sq. ft. 60 min |  | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs |  | 1-1/8" / 9.0 lbs standard (7/8" thin profile also available) |  |  | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs |  |  | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs |  | 7/8" / 11.3 lbs |  |  |  | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs |  | 1" / 10.3 lbs |  |  |  |  | 1" / 12.3 lbs
Thickness/Weight per sq. ft. 90 min |  |  | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs |  |  | 1-1/2'' / 12.0 lbs |  | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs |  |  | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs |  |  | 1-7/16" / 17.6 lbs |  |  | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs |  |  | 1-1/2" / 14.6 lbs |  |  |  |  | 1-3/16" / 16.4 lbs
Thickness/Weight per sq. ft. 120 min | [7 empty] | 1-1/2'' / 12.0 lbs |  | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs |  |  |  |  | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs |  |  |  | 2 -1/4" / 22.9 lbs |  |  | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs |  |  |  | 1-9/16" / 15.8 lbs |  |  |  |  | 2-1/8" / 24.6 lbs
Thickness/Weight per sq. ft. 3 hours | [9 empty] | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs |  |  |  |  | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | [6 empty] | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs
Max sq. In. 20 min | 5,760 for Windows, Sidelites & Transoms Requires AHJ approval 3,436 for Aluminum Doors 3,341 for Steel Doors 3,299 for Wood Doors | 5,760 for Steel Windows, Sidelites & Transoms 3,341 for Steel Doors | 4,608 for Windows & Sidelites 3,456 for Transoms 3,289 for Steel Doors 2,856 for Wood Doors | [5 empty] | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Doors | 3,204 for Doors Only | 1,296 for Interior Doors Only | 1,296 for Windows, Sidelites & Transoms 3,289 for Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors |  |  |  |  | 3,419 for Doors Only |  |  |  | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | [5 empty] | 3,154 for Steel Windows & Doors Only 2,868 for Wood Doors Only
Max sq. In. 45 min |  | 5,760 for Steel Windows, Sidelites & Transoms Requires AHJ approval 3,341 for Steel Doors Requires AHJ approval | 4,608 for Windows & Sidelites 3,456 for Transoms 2,856 for Steel Doors 1,296 for Wood Doors | 100 | 4952 |  |  |  | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Doors |  |  | 1,296 for Windows, Sidelites, Transoms & Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 4,500 for Windows, Sidelites & Transoms 3,724 for Doors |  |  |  |  | 2,736 for Windows, Sidelites & Transoms Only | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Doors | 3,419 for Windows, Sidelites & Transoms 3,419 for Doors |  |  |  |  | 4,608 for Windows & Sidelites 2,747 for Doors
Max sq. In. 60 min |  | 3,388 for Steel Windows, Sidelites & Transoms (Non-Temperature Rise) Requires AHJ approval 3,341 for Non-Temperature Rise Steel Doors Requires AHJ approval | 960 for Non-Temperature Rise Wood Doors 552 for Non-Temperature Rise Steel Doors 100 for Temperature Rise Doors | 100 |  | 4952 |  |  | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  |  | 960 for Non-Temperature Rise Wood Doors (when glazed with Pemko FG3000) 100 for Temperature Rise Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  | 5,605 for Windows, Sidelites & Transoms 3,724 for Non-Temperature Rise Doors 3,724 for Temperature Rise Doors |  |  |  | 2,736 for Windows, Sidelites & Transoms Only | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  | 4,449 for Windows, Sidelites & Transoms 2,685 for Non-Temperature Rise Doors 2,685 for Temperature Rise Doors |  |  |  |  | 4,487 for Wall Systems 3,855 for Windows, Sidelites & Transoms 3,855 for Doors
Max sq. In. 90 min |  |  | 552 for Non-Temperature Rise Steel Doors 100 for Temperature Rise Doors | 100 |  |  | 4876 |  | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  |  | 552 for Non-Temperature Rise Doors (when glazed with Pemko FG3000) 100 for Temperature Rise Doors | 2,627 for Windows, Sidelites & Transoms Only | 2,627 for Windows, Sidelites & Transoms 2,034 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,627 for Windows, Sidelites & Transoms 2,034 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  |  | 3,724 for Windows, Sidelites & Transoms 3,724 for Non-Temperature Rise Doors 3,724 for Temperature Rise Doors |  |  | 2,736 for Windows, Sidelites & Transoms Only | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors |  |  | 3,174 for Windows, Sidelites & Transoms 3,174 for Non-Temperature Rise Doors 3,174 for Temperature Rise Doors |  |  |  |  | 1,103 for Wall Systems 3,465 for Windows, Sidelites & Transoms 2,196 for Doors
Max sq. In. 120 min | [7 empty] | 4876 |  | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) |  |  |  |  | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) |  |  |  | 3,724 for Windows, Sidelites & Transoms Only |  |  | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) |  |  |  | 4,435 for Windows, Sidelites & Transoms Only |  |  |  |  | 3,828 for Wall Systems Only
Max sq. In. 3 hours | [9 empty] | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) |  |  |  |  | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | [6 empty] | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise)
Cost
Warranty | Lifetime | Lifetime | 10 years | Lifetime | 5 Years | 5 Years | 5 Years | 5 Years | 10 Years | 10 Years | 5 Years | No warranty | 5 years | 3 years | No warranty | 3 years | 5 years | 5 years | 5 years | 5 years | 5 years | No warranty | No warranty | 3 years | 5 years | 3 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years
IBC Markings | D-20 | D-NT-20/45/60 | D-H-OH-NT-20/45/60/90 | D-H-45/60/90 | D-H-OH-T-45 | D-H-T-W-60 | D-H-T-W-90 | D-H-T-W-120 | D-H-OH-NT-20/45/60/90 | D-H-OH-NT-20/45/60/90/180 | D-H-OH-NT-20/45/60/90/180
Approved Testing | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, CPSC 16 CFR 1201 Cat. II. This product requires AHJ approval for 45-60 min applications because it does not pass the hose stream portion of the fire test. | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-2 (1997), UBC 7-4 (1997), NFPA 80, NFPA 257, ASTM E2074-00, ASTM E2010-01, ULC CAN4-S106 | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2, UBC 7-4, NFPA 252, ASTM E2074, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2, UBC 7-4, NFPA 252, ASTM E2074, CSFM 43.7, CPSC 16 CFR 1201 Cat. I | UL 9, UL 10C, UBC 7-2, UBC 7-4, NFPA 252, NFPA 257, ASTM E2074, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 257, CAN4 S-104, CSFM 43.7 | UL 9, UL 10B, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, CAN4 S-104, CAN4 S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, CAN4 S-104, CAN4 S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 10C, NFPA 80, NFPA 252, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106 | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 263, NFPA 251, ASTM E119, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2 (1997), NFPA 252, ASTM E-152, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-2 (1997), UBC 7-4 (1997), NFPA 252, NFPA 257, ASTM E119, ASTM E2010-99, CAN 4S-105, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UL 263, UBC 7-1 (1997), UBC 7-2 (1997), UBC 7-4 (1997), NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2010-99, CAN 4S-101, CAN 4S-104, CAN 4S-105, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-1 (1997), UBC 7-2 (1997), UBC 7-4 (1997), NFPA 251, NFPA 257, ASTM E119, ASTM E152, ASTM E163, CAN 4S-104, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 263, UBC 7-1 (1997), NFPA 251, ASTM E119, CAN 4S-101, CPSC 16 CFR 1201 Cat. II
Listing Agency | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL & Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc.

## PYRAN Comparison
CRITERIA | PYRAN Platinum | PYRAN Platinum F | PYRAN Platinum L | FireLite / Keralite Standard R | FireLite NT / Keralite Standard F / Keralite Select F | FireLite Plus by TGP / Keralite Standard L / Keralite Select L | Keralite Ultra | SuperLite I | SuperLite X-45/60/90 | SuperLite II-XL 45
FIRE RATING | 20 min. to 90 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 90 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 45 min. to 3 hrs. with hose stream | 20 min. without hose stream | 45 min. to 90 min. with hose stream | 45 min. with hose stream
ORIGIN FOR GLAZING | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA
GLASS MAKE-UP | Ceramic | Filmed Ceramic | Laminated Ceramic | Ceramic | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic | Clear Tempered. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Specialty Glass | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option.
VISUAL APPEARANCE | Slight Tint | Slight Tint | Slight Tint | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Clear | Clear | Clear
THICKNESS/WEIGHT PER SQ. FT. | 3/16” / 2.5 lbs | 3/16” / 2.5 lbs | 3/8" / 4.0 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0-4.1 lbs | 3/4" / 7.5 lbs | 1/4" / 3.0 lbs | 3/4" / 9.0 lbs | 3/4" / 8.0 lbs standard (1/2" thin profile also available)
WINDOWS, SIDELITES & TRANSOMS | 3323 | 3323 | 3143 | 3,325 for FireLite (2,627 for 90 min.) 2,736 for Keralite Standard R | 3,325 for FireLite NT (2,627 for 90 min.) 3,627 for Keralite Standard F & Select F (2,736 for 90 min.) | 3,325 for FireLite Plus (2,627 for 90 min.) 3,627 for Keralite Standard L & Select L (2,736 for 90 min.) | 2736 | 5,760 for 20 min. (Requires AHJ approval) | N/A | 4952
20-90 MINUTE DOORS (NT) | N/A | 2799 | 2736 | N/A | 3,204 for FireLite NT (2,034 for 90 min.) 3,627 for Keralite Standard F & Select F (3,534 for 90 min.) | 3,204 for FireLite Plus (2,034 for 90 min.) 3,627 for Keralite Standard L & Select L (3,534 for 90 min.) | 2736 | 3,436 for 20 min. Aluminum Doors 3,341 for 20 min. Steel Doors 3,299 for 20 min. Wood Doors | 100 | 4952
60-90 MINUTE DOORS (T) | N/A | 100 | 100 | N/A | 100 | 100 | 100 | N/A | 100 | N/A
ACOUSTICAL BARRIER | Approx. STC 35 | Approx. STC 35 | Approx. STC 36 | Approx. STC 35 | Approx. STC 35 | Approx. STC 37-38 | Approx. STC 38 | Approx. STC 28 | Approx. STC 38 | Approx. STC 40
RADIANT HEAT PROTECTION (ASTM E-119) | No | No | No | No | No | No | No | No | No | Yes
SAFETY RATING | No | CSPC Cat. I & II | CSPC Cat. I & II | No | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II
VERSATILITY | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated / Decorative | Decorative | Insulated / Ballistic / Blast / Decorative / Hurricane
COST | $$ | $$ | $$ | $$$ | $$$ | $$$ | $$$ | $ | $ | $
WARRANTY | 10 Years | 10 Years | 5 Years | No Warranty | 3 Years | 5 Years | 5 Years | Lifetime | Lifetime | 5 Years standard 10 Years optional

## II-XL 45 Comp.
CRITERIA | SuperLite II-XL 45 | Pyrostop 45 | Contraflam 45 | Pyrobel 45 | PYRAN Platinum F / FireLite NT / Keralite Standard F / Keralite Select F | PYRAN Platinum L / FireLite Plus / Keralite Standard L / Keralite Select L | Keralite Ultra
FIRE RATING | 45 min. with hose stream | 45 min. with hose stream | 45 min. with hose stream | 45 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 45 min. to 3 hrs. with hose stream
ORIGIN FOR GLAZING | Manufactured in the USA | Imported | Manufactured in the USA | Imported | Imported | Imported | Imported
GLASS MAKE-UP | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Annealed | Tempered | Annealed | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic
VISUAL APPEARANCE | Clear | Clear | Clear | Clear | Tint | Tint | Amber Tint
THICKNESS/WEIGHT PER SQ. FT. | 3/4" / 8.0 lbs standard (1/2" thin profile also available) | 3/4" / 9.2 lbs | 3/4" / 8.0 lbs | 5/8" / 8.2 lbs | 3/16" / 2.4-2.5 lbs | 5/16"-3/8" / 4.0-4.1 lbs | 3/4" / 7.5 lbs
45 MINUTE WINDOWS, SIDELITES & TRANSOMS | 4952 | 4500 | 3419 | 4608 | 3,323 for PYRAN Platinum F 3,325 for FireLite NT 3,627 for Keralite Standard F & Select F | 3,143 for PYRAN Platinum L 3,325 for FireLite Plus 3,204 for Keralite Standard L & Select L | 2736
45 MINUTE DOORS (NT) | 4952 | 3724 | 3419 | 2747 | 2,799 for PYRAN Platinum F 3,204 for FireLite NT 3,627 for Keralite Standard F & Select F | 2,736 for PYRAN Platinum L 3,204 for FireLite Plus 3,627 for Keralite Standard L & Select L | 2736
ACOUSTICAL BARRIER | Approx. STC 40 | Approx. STC 40 | Approx. STC 39 | Approx. STC 39 | Approx. STC 35 | Approx. STC 36-38 | Approx. STC 38
RADIANT HEAT PROTECTION (ASTM E-119) | Yes | Yes | Yes | Yes | No | No | No
SAFETY RATING | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
VERSATILITY | Insulated / Ballistic / Blast / Decorative / Hurricane | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated
COST | $ | $$ | $$ | $$ | $$ | $$$ | $$$
WARRANTY | 5 Years standard 10 Years optional | 5 Years | 5 Years | 5 Years | 10 Years for PYRAN Platinum F 3 Years for others | 5 Years | 5 Years

## II-XL 60 Comp.
CRITERIA | SuperLite II-XL 60 | Pyrostop 60 | Contraflam 60 | Pyrobel 60 | PYRAN Platinum F / FireLite NT / Keralite Standard F / Keralite Select F | PYRAN Platinum L / FireLite Plus / Keralite Standard L / Keralite Select L | Keralite Ultra
FIRE RATING | 60 min. with hose stream | 60 min. with hose stream | 60 min. with hose stream | 60 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 45 min. to 3 hrs. with hose stream
ORIGIN FOR GLAZING | Manufactured in the USA | Imported | Manufactured in the USA | Imported | Imported | Imported | Imported
GLASS MAKE-UP | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Annealed | Tempered | Annealed | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic
VISUAL APPEARANCE | Clear | Clear | Clear | Clear | Tint | Tint | Amber Tint
THICKNESS/WEIGHT PER SQ. FT. | 1-1/8" / 9.0 lbs standard (7/8" thin profile also available) | 7/8" / 11.3 lbs | 1" / 10.3 lbs | 1" / 12.3 lbs | 3/16" / 2.4-2.5 lbs | 5/16"-3/8" / 4.0-4.1 lbs | 3/4" / 7.5 lbs
60 MINUTE WINDOWS, SIDELITES & TRANSOMS | 4952 | 5605 | 4449 | 3855 | 3,323 for PYRAN Platinum F 3,325 for FireLite NT 3,627 for Keralite Standard F & Select F | 3,143 for PYRAN Platinum L 3,325 for FireLite Plus 3,204 for Keralite Standard L & Select L | 2736
60 MINUTE DOORS (NT) | 4952 | 3724 | 2685 | 3855 | 2,799 for PYRAN Platinum F 3,204 for FireLite NT 3,627 for Keralite Standard F & Select F | 2,736 for PYRAN Platinum L 3,204 for FireLite Plus 3,627 for Keralite Standard L & Select L | 2736
60 MINUTE DOORS (T) | 4952 | 3724 | 2685 | 3855 | 100 | 100 | 100
ACOUSTICAL BARRIER | Approx. STC 42 | Approx. STC 41 | Approx. STC 40 | Approx. STC 42 | Approx. STC 35 | Approx. STC 36-38 | Approx. STC 38
RADIANT HEAT PROTECTION (ASTM E-119) | Yes | Yes | Yes | Yes | No | No | No
SAFETY RATING | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
VERSATILITY | Insulated / Ballistic / Blast / Decorative / Hurricane | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated
COST | $ | $$ | $$ | $$ | $$ | $$$ | $$$
WARRANTY | 5 Years standard 10 Years optional | 5 Years | 5 Years | 5 Years | 10 Years for PYRAN Platinum F 3 Years for others | 5 Years | 5 Years

## II-XL 90 Comp.
CRITERIA | SuperLite II-XL 90 | Pyrostop 90 | Contraflam 90 | Pyrobel 90 | PYRAN Platinum F / FireLite NT / Keralite Standard F / Keralite Select F | PYRAN Platinum L / FireLite Plus / Keralite Standard L / Keralite Select L | Keralite Ultra
FIRE RATING | 90 min. with hose stream | 90 min. with hose stream | 90 min. with hose stream | 90 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 45 min. to 3 hrs. with hose stream
ORIGIN FOR GLAZING | Manufactured in the USA | Imported | Manufactured in the USA | Imported | Imported | Imported | Imported
GLASS MAKE-UP | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Annealed | Tempered | Annealed | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic
VISUAL APPEARANCE | Clear | Clear | Clear | Clear | Tint | Tint | Amber Tint
THICKNESS/WEIGHT PER SQ. FT. | 1-1/2'' / 12.0 lbs | 1-7/16" / 17.6 lbs | 1-1/2" / 14.6 lbs | 1-3/16" / 16.4 lbs | 3/16" / 2.4-2.5 lbs | 5/16"-3/8" / 4.0-4.1 lbs | 3/4" / 7.5 lbs
90 MINUTE WINDOWS, SIDELITES & TRANSOMS | 4876 | 3724 | 3174 | 3465 | 3,323 for PYRAN Platinum F 2,627 for FireLite NT 2,736 for Keralite Standard F & Select F | 3,143 for PYRAN Platinum L 2,627 for FireLite Plus 2,736 for Keralite Standard L & Select L | 2736
90 MINUTE DOORS (NT) | 4876 | 3724 | 3174 | 2196 | 2,799 for PYRAN Platinum F 2,034 for FireLite NT 3,534 for Keralite Standard F & Select F | 2,736 for PYRAN Platinum L 2,034 for FireLite Plus 3,534 for Keralite Standard L & Select L | 2736
90 MINUTE DOORS (T) | 4876 | 3724 | 3174 | 2196 | 100 | 100 | 100
ACOUSTICAL BARRIER | Approx. STC 44 | Approx. STC 45 | Approx. STC 45 | Approx. STC 43 | Approx. STC 35 | Approx. STC 36-38 | Approx. STC 38
RADIANT HEAT PROTECTION (ASTM E-119) | Yes | Yes | Yes | Yes | No | No | No
SAFETY RATING | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
VERSATILITY | Insulated / Ballistic / Blast / Decorative / Hurricane | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated
COST | $ | $$ | $$ | $$ | $$ | $$$ | $$$
WARRANTY | 5 Years standard 10 Years optional | 5 Years | 5 Years | 5 Years | 10 Years for PYRAN Platinum F 3 Years for others | 5 Years | 5 Years

## II-XL 120 Comp.
CRITERIA | SuperLite II-XL 120 | Pyrostop 120 | Contraflam 120 | Pyrobel 120 | PYRAN Platinum F / FireLite NT / Keralite Standard F / Keralite Select F | PYRAN Platinum L / FireLite Plus / Keralite Standard L / Keralite Select L | Keralite Ultra
FIRE RATING | 120 min. with hose stream | 120 min. with hose stream | 120 min. with hose stream | 120 min. with hose stream | 20 min. to 3 hrs. with hose stream | 20 min. to 3 hrs. with hose stream | 45 min. to 3 hrs. with hose stream
ORIGIN FOR GLAZING | Manufactured in the USA | Imported | Manufactured in the USA | Imported | Imported | Imported | Imported
GLASS MAKE-UP | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Annealed | Tempered | Annealed | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic
VISUAL APPEARANCE | Clear | Clear | Clear | Clear | Tint | Tint | Amber Tint
THICKNESS/WEIGHT PER SQ. FT. | 1-1/2'' / 12.0 lbs | 2 -1/4" / 22.9 lbs | 1-9/16" / 15.8 lbs | 2-1/8" / 24.6 lbs | 3/16" / 2.4-2.5 lbs | 5/16"-3/8" / 4.0-4.1 lbs | 3/4" / 7.5 lbs
120 MINUTE WINDOWS, SIDELITES & TRANSOMS | 4876 | 3724 | 4435 | 3828 | N/A | N/A | N/A
ACOUSTICAL BARRIER | Approx. STC 44 | Approx. STC 46 | Approx. STC 46 | Approx. STC 46 | Approx. STC 35 | Approx. STC 36-38 | Approx. STC 38
RADIANT HEAT PROTECTION (ASTM E-119) | Yes | Yes | Yes | Yes | No | No | No
SAFETY RATING | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
VERSATILITY | Insulated / Ballistic / Blast / Decorative / Hurricane | Insulated | Insulated | Insulated | Insulated | Insulated | Insulated
COST | $ | $$ | $$ | $$ | $$ | $$$ | $$$
WARRANTY | 5 Years standard 10 Years optional | 5 Years | 5 Years | 5 Years | 10 Years for PYRAN Platinum F 3 Years for others | 5 Years | 5 Years