Welcome to the SAFTIFIRSTTM Guide Specification System prepared as an aid to specifiers in preparing written construction documents.  For specification assistance with specific product applications, please contact SAFTIFIRSTTM.  To download an electronic copy, please visit www.safti.com.

SPECIFICATION

SECTION 08 8810: FIRE RATED GLASS & FRAMING

SAFTIfireTM HMTR Door Framing

##### PART 1 GENERAL

1.01 SUMMARY

- Section Includes: Fire rated framing system.

- SAFTIfire HMTR Framing 60-90 minute temperature rise framing system for interior and exterior applications.

- Applications of fire rated framing includes:

  - Vision lites in fire rated doors and full vision fire rated doors with fire rating requirement as specified.

- Related Sections:

- Section 01 3323:  Shop Drawings, Product Data and Samples.

- Section 08 1110:  Steel Doors and Frames.

- Section 08 1113:  Hollow Metal Doors and Frames

- Section 08 7100:  Finish Hardware.

1.02 REFERENCES

- American Society for Testing and Materials (ASTM):

- ASTM E152: Methods of Fire Tests of Door Assemblies.

- ASTM E2074: Standard Test Method for Fire Tests of Door Assemblies, including Positive Pressure Testing of Side-hinged and Pivoted Swinging Door Assemblies.

- National Fire Protection Association (NFPA):

- NFPA 80: Fire Doors and Windows.

- NFPA 252: Fire Tests of Door Assemblies.

- Underwriters Laboratories, Inc. (UL):

- UL 9: Fire Tests of Door Assemblies.

- UL 10 C: Fire Tests of Door Assemblies.

- Standard Council of Canada (ULC):

- ULC Standard CAN4-S104:  Fire Tests of Door Assemblies.

- ULC Standard CAN4-S106:  Fire Tests of Window Assemblies.

E.	Consumer Product Safety Commission (CPSC):

- CPSC 16 CFR 1201: Safety Standard for Architectural Glazing Materials.

F.  Glass Association of North America (GANA)

1.  GANA – Glazing Manual.

2.  FGMA – Sealant Manual.

G.  [American Recovery and Reinvestment Act

1. Section 1605, Title XVI Buy American Provision]

H.  [Insert building code used by Authority Having Jurisdiction]

1.03 SYSTEM DESCRIPTION

- Performance Requirements:

- Fire Rating: 60 or 90 minutes for temperature rise doors as specified.

- Door Certifications:  Doors shall be tested in accordance with ASTM E2074-00, NFPA 252, UL 10b or CAN4-S104 Standard Test Methods of Fire Tests of Door Assemblies.

- Testing Laboratory: Fire test shall be conducted by a nationally recognized independent testing laboratory.

- Listings and Labels:

- Fire rated framing system shall be under current follow-up service by a nationally recognized independent laboratory approved by OSHA and maintain a current listing or certification.  Assemblies shall be labeled in accordance with limits of listings.

1.04 SUBMITTALS

- Submit listed submittals in accordance with Conditions of the Contract and Division 1 Submittal Procedure Section.

- Shop Drawings: Submit shop drawings showing layout, profiles and product components.

- Samples: Submit samples for finishes, colors and textures.

- Technical Information: Submit latest edition of manufacturer’s product data.

1.05 DELIVERY, STORAGE AND HANDLING

- General:  Comply with Division 1 Product Requirements Sections.

- Ordering: Comply with manufacturer’s ordering instructions and lead-time requirements to avoid construction delays.

- Delivery:  Deliver materials to specified destinations in manufacturer’s or distributor’s packaging undamaged, complete with installation instructions.

- Storage and Protection: Store off ground, under cover, protected from weather and construction activities and at temperature conditions recommended by manufacturer.

1.06 FABRICATION DIMENSIONS

A.  Field Measurements: Verify actual measurements for openings by field measurements before fabrication.  Show recorded measurements on shop drawings.  Coordinate field measurements and fabrication schedule with construction progress to avoid construction delays.

1.07 WARRANTY

- Project Warranty: Refer to Conditions of the Contract for project warranty provisions.

- Manufacturer’s Warranty: Submit, for Owner’s acceptance, manufacturer’s standard warranty document.  Manufacturer’s warranty is not intended to limit other rights that the Owner may have under the Contract Documents.

###### PART 2 PRODUCTS

2.01 MANUFACTURERS – FIRE RATED (DOOR)

A.  Manufacturer of Framing System: SAFTIfireTM HMTR Framing as manufactured and distributed by SAFTI FIRSTTM Fire Rated Glazing Solutions,

1. Contact:  100 N Hill Drive, Suite 12, Brisbane, CA 94005; Telephone 888.653.

3333; Fax 888.653.4444; email info@safti.com; Web site www.safti.com

B.  Manufacturer of Glazing Material: (SuperLite TM II-XL) (SuperLite TM II-XL IGU) to maximum size tested.  (SuperLite TM I-XL) (SuperLite TM I-XL IGU) (SuperLite TM I-W) (PYRAN® Platinum F) (PYRAN® Platinum F IGU) (PYRAN® Platinum L) (PYRAN® Platinum L IGU) limited to 100 square inches.  All SuperLite TM products are manufactured and distributed by SAFTI FIRST TM Fire Rated Glazing Solutions.  PYRAN® Platinum is manufactured by SCHOTT Technical Glass Solutions and  distributed by SAFTI FIRST TM Fire Rated Glazing Solutions.

1. Contact:  100 N Hill Drive, Suite 12, Brisbane, CA 94005; Telephone 888.653.

3333; Fax 888.653.4444; email info@safti.com; Web site www.safti.com

C.  Fire rated glass and framing must be provided by a single-source, US manufacturer. Distributors of fire rated glass and framing are not to be considered as manufacturers.

D.  Substitutions:  No substitutions allowed.

2.02 MATERIALS – FRAMING

A.  Temperature rise framing system rated for 60 to 90 minutes for use in doors.

B.  Properties:

1.  Constructed in accordance with the individual manufacturer’s listings or in accordance

with HMMA 861-08 and HMMA 850.

2.03  MATERIALS – GLASS

- Assemblies shall be glazed with SuperLiteTM glazing products.

- Properties:

- Individual Lites shall be permanently identified with a listing mark.

- Glazing material installed in “Hazardous Locations” (subject to human impact) shall be certified to meet the applicable requirements for fire rated assemblies referenced in ANSI Z97.1 Standard for Safety Glazing Materials Used In Buildings and/or CPSC 16 CFR 1201 Safety Standard for Architectural Glazing Materials.

- Temperature rise on the unexposed side of glazing material shall be limited to 450 degrees Fahrenheit when required.

- Visible daylight transmission: Varies by glazing type.  Refer to SuperLiteTM product data for more information.

- STC rating:  Varies by glazing type. Refer to SuperLiteTM product data for more information.

C.  Logo: Each piece of fire rated glazing shall be labeled with a permanent logo.

2.03 FABRICATION

- Assemblies shall be furnished [knocked down for field assembly and will be glazed in the field]   [assembled (should configurations and job site conditions allow)]    [unitized (should configurations and job site conditions allow)] .

- Door assemblies shall be factory prepared for field mounting of hardware.

- Fabrication Dimensions:  Fabricate to approved dimensions.  The general contractor shall guarantee dimensions within required tolerance.  Obtain approved shop drawings prior to fabrication.

2.04 FINISHES

A. High performance fluoropolymer finishes by PPG.

2.05  DOOR HARDWARE FOR SINGLE AND PAIRED DOORS

- Hardware shall be supplied with the fire door. Hardware selection shall be from door manufacturer’s standard recommended hardware groups as specified below.

- Provide high traffic areas of areas requiring a door motion force of greater than 15 lbs. with power assisted hardware for use with manufacturer’s frame system.

- Standard operating hardware for single and pair doors doors.

| Quantity | Item | Description | Manufacturer | Finish |
| --- | --- | --- | --- | --- |
| 4 | Hinges | 5 Knuckle Ball Bearing Heavy Duty Butt Hinges | Hager BB1168 | US32D |
| 1 | Panic Device | 17 Series Touch Bar Panic with Surface vertical Rods | Monarch F-X-VV | US32D |
| 1 | Closing Device | Heavy-duty Surface Applied Closer | LCN 4041 | Aluminum |
| 1 | Auto Door Bottoms | 420APKL | Pemko |  |

PART 3 EXECUTION

3.01 MANUFACTURER’S INSTRUCTIONS

- Compliance:  Comply with manufacturer’s product data including product technical bulletins and installation instructions.

3.02 EXAMINATION

- Site Verification of Conditions: Verify substrate conditions, have been previously installed under other sections, and are acceptable for product installation in accordance with manufacturer’s instructions.  Openings shall be plumb, square and within allowable tolerances.  The Architect/Engineer shall be notified of any conditions that jeopardize the integrity of the proposed fire wall/door framing system.  Do not proceed until such conditions are corrected.

3.03 INSTALLATION

- Fire door/window installation shall be by a licensed contractor and in strict accordance with the approved shop drawings.

3.04 CLEANING AND PROTECTION

A.  Protect glass from contact with contaminating substances resulting from construction

operations.  Remove such substances by method approved by manufacturer.

B.   Wash glass on both faces not more than four days prior to date schedule for inspections

intended to establish date of Substantial Completion.  Wash glass by method

recommended by glass manufacturer.

C.  Remove temporary coverings and protection of adjacent work areas.

D.  Remove construction debris from project site and legally dispose of debris.

END OF SECTION

In the interest of continuous improvement of its product line, SAFTIFIRSTTM reserves the right to modify its products’ composition, colors, textures, sizes, and other physical and performance attributes and these guide specifications at any time. SAFTIFIRSTTM makes no expressed or implied warranties regarding content, errors, or omissions in the information presented. Specifications modified or rewritten not in conformance with manufacturer’s standard processes, products, and procedures may void warranties and related remedies.