Recommended Update to Master Specification – Division 8: Glazing
Part 2: Products – Fire Rated Glass Schedule

A.  Fire Protective Glazing – tested to NFPA 252/257 and listed and labeled by UL and/or Intertek/Warnock-Hersey.  Where safety glazing is required, fire rated glass shall meet CPSC 16 CFR 1201 Category I or II.

1.  20 minute doors – clear, fully tempered float glass for 20 min. door applications without hose stream.  Meets NFPA 252/257 and CPSC Category II impact safety.  Wire and tint-free appearance.  Made in the USA.  Basis of Design:  SuperLite I by SAFTI FIRST (www.safti.com ; 888.653.3333) or approved equal.

2.  45 minute doors, sidelites, transoms and openings with hose stream – clear, fully tempered fire protective glass units with hose stream.  Meets NFPA 252/257/251, ASTM E-119 and CPSC Category II impact safety.  Wire and tint-free appearance.   Made in the USA.  Basis of Design:  SuperLite II-XL 45 by SAFTI FIRST (www.safti.com ; 888.653.3333) or approved equal.

3.  45 minute doors, sidelites, transoms and openings without hose stream (AHJ approval may be required) – clear, fully tempered float glass tested to NFPA 252/257 without hose stream.  Meets CPSC Category II impact safety.  Wire and tint-free appearance.   Made in the USA.  Basis of Design:  SuperLite I-XL by SAFTI FIRST  (www.safti.com ; 888.653.3333).  AHJ approval may be required.

4.  Safety rated wired glass – filmed wired glass for fire protective doors, sidelites, transoms and openings with hose stream.  Meets NFPA 252/257 and CPSC Category II impact safety.  Tint-free appearance.  Made in the USA.  Basis of Design:  SuperLite I-W by SAFTI FIRST (www.safti.com ; 888.653.3333).

5.  60-90 minute door vision lites up to 100 sq. in. – for use in 60 and 90 minute temperature rise doors with hose stream.  Limited to 100 sq. in.  Meets NFPA 252 and CPSC Category I impact safety.  Wire and tint-free appearance.  Made in the USA.  Basis of Design:  SuperLite X-90 by SAFTI FIRST (www.safti.com ; 888.653.3333).

B.  Fire Resistive Glazing – tested to ASTM E-119/NFPA 251/UL 263 with hose stream.   Listed and labeled by UL and/or Intertek/Warnock-Hersey.  Where safety glazing is required, fire rated glass shall meet CPSC 16 CFR 1201 Category I or II.

1.  60-120 minute wall, window or door applications – clear, fire resistive tempered units with hose stream.  Meets ASTM E-119/NFPA 251/UL 263 and CPSC Cat. II impact safety.  Wire and tint-free appearance.  Made in the USA.  Basis of Design:  SuperLite II-XL 60-120 by SAFTI FIRST (www.safti.com ; 888.653.3333) or approved equal.

Note:  All applications are subject to compliance with current building, safety and fire code requirements.