## Working Sheet - ALL PRODUCTS
| SuperLite I | SuperLite I-XL | SuperLite I-W | SuperLite X-45/60/90 | SuperLite II-XL 45 | SuperLite II-XL 60 | SuperLite II-XL 90 | SuperLite II-XL 120 | Pyran Platinum | Pyran Platinum F | Pyran Platinum L | Fireglass 20 | Pyrodur | WireLite NT | FireLite | FireLite NT | FireLite Plus | Pyrostop 45 | Pyrostop 60 | Pyrostop 90 | Pyrostop 120 | Pyroswiss | Keralite Standard R (FR-R) | Keralite Standard F (FR-F) | Keralite Standard L (FR-L) | Keralite Select F | Keralite Select L | Keralite Ultra | Contraflam 45 (Swissflam) | Contraflam 60 | Contraflam 90 | Contraflam 120 | PyroEdge 20 | Pyrobel 45 | Pyrobel 60 | Pyrobel 90 | Pyrobel 120
Fire Rating | 20 min | 20 min - 60 min | 20 min - 90 min | 45 min - 90 min | 45 min | 60 min | 90 min | 120 min | 20 min - 90 min | 20 min - 3 hours | 20 min - 3 hours | 20 min | 20 min | 20 min - 90 min | 20 min - 90 min | 20 min - 3 hours | 20 min - 3 hours | 45 min | 60 min | 90 min | 120 min | 20 min | 20 min - 90 min | 20 min - 3 hours | 20 min - 3 hours | 20 min - 3 hours | 20 min - 3 hours | 20 min - 3 hours | 45 min | 60 min | 90 min | 120 min | 20 min | 45 min | 60 min | 90 min | 120 min
Origin for Glazing | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Imported | Imported | Imported | Manufactured in the USA | Imported | Unknown | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Imported | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Manufactured in the USA | Imported | Imported | Imported | Imported
Glass Make-up | Clear Tempered. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Specialty Tempered | Safety Filmed Wired Glass | Specialty Glass | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Comprised of inboard and outboard tempered lites protecting a fire resistive intumescent interlayer. Available with Starphire® Ultra-Clear Glass by PPG as an option. | Ceramic | Filmed Ceramic | Laminated Ceramic | Tempered | Annealed | Safety Filmed Wired Glass | Ceramic | Filmed Ceramic | Laminated Ceramic | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Tempered | Ceramic | Filmed Ceramic | Laminated Ceramic | Filmed Ceramic | Laminated Ceramic | Laminated Ceramic | Composed of multiple sheets of tempered glass laminated with an intumescent interlayer. | Composed of multiple sheets of tempered glass laminated with an intumescent interlayer. | Composed of multiple sheets of tempered glass laminated with an intumescent interlayer. | Composed of multiple sheets of tempered glass laminated with an intumescent interlayer. | Tempered | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer. | Composed of multiple sheets of annealed glass laminated with an intumescent interlayer.
Visual Appearance | Clear | Clear | Clear with Wire | Clear | Clear | Clear | Clear | Clear | Neutral. No polishing required, with savings passed to customer. | Neutral. No polishing required, with savings passed to customer. | Neutral. No polishing required, with savings passed to customer. | Clear | Clear | Clear with Wire | Amber Tint. Polishing required for premium-priced version. | Amber Tint. Polishing required for premium-priced version. | Amber Tint. Polishing required for premium-priced version. | Clear | Clear | Clear | Clear | Clear | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Amber Tint | Clear | Clear | Clear | Clear | Clear | Clear | Clear | Clear | Clear
Light Transmission | Approx. 89.5% | Approx. 81% | Approx. 86% | Approx. 81% | Approx. 85-90% | Approx. 85-90% | Approx. 81-89% | Approx. 81-89% | Unknown | Unknown | Unknown | Approx. 89% | Approx. 78% | Approx. 77% | Approx. 88% | Approx. 88% | Approx. 85% | Approx. 86% | Approx. 87% | Approx. 84% | Approx. 74-75% | Approx. 89% | Approx. 88% | Approx. 88% | Approx. 82% | Approx. 88% | Approx. 82% | Approx. 79% | Approx. 84% | Approx. 85% | Approx. 82% | Approx. 82% | Approx. 87-89% | Approx. 85% | Approx. 81% | Approx. 82% | Approx. 71%
ASTM E-119 Heat Barrier | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | No | No | No | Yes | Yes | Yes | Yes | No | No | No | No | No | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes
Impact Safety Rating | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | CSPC Cat. I & II | Not safety rated | CSPC Cat. I & II | CSPC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I only | CPSC Cat. I & II | Not safety rated | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | Not safety rated | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II | CPSC Cat. I & II
Hose Stream | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes
Acoustical Barrier | Approx. STC 28 | Approx. STC 28 | Approx. STC 28 | Approx. STC 38 | Approx. STC 40 | Approx. STC 42 | Approx. STC 44 | Approx. STC 44 | Approx. STC 35 | Approx. STC 35 | Approx. STC 36 | No | No | No | Approx. STC 35 | Approx. STC 35 | Approx. STC 38 | Approx. STC 40 | Approx. STC 41 | Approx. STC 45 | Approx. STC 46 | Approx. STC 32 | Approx. STC 35 | Approx. STC 35 | Approx. STC 37 | Approx. STC 35 | Approx. STC 37 | Approx. STC 38 | Approx. STC 39 | Approx. STC 40 | Approx. STC 45 | Approx. STC 46 | No | Approx. STC 39 | Approx. STC 42 | Approx. STC 43 | Approx. STC 46
Thickness/Weight per sq. ft. 20 min | 1/4" / 3.0 lbs | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | N/A | N/A | N/A | N/A | N/A | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | 1/4" / 3.0 lbs | 5/16" / 3.48 lbs | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | N/A | N/A | N/A | N/A | 1/4" / 3.2 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | N/A | N/A | N/A | N/A | 1/4" / 3.0 lbs or 3/8" / 4.5 lbs | N/A | N/A | N/A | N/A
Thickness/Weight per sq. ft. 45 min | N/A | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs | 3/4" / 8.0 lbs standard (1/2" thin profile also available) | N/A | N/A | N/A | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | N/A | N/A | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | 3/4" / 9.2 lbs | N/A | N/A | N/A | N/A | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | 3/4" / 8.0 lbs | N/A | N/A | N/A | N/A | 5/8" / 8.2 lbs | N/A | N/A | N/A
Thickness/Weight per sq. ft. 60 min | N/A | 1/4" / 3.0 lbs | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs | N/A | 1-1/8" / 9.0 lbs standard (7/8" thin profile also available) | N/A | N/A | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | N/A | N/A | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | N/A | 7/8" / 11.3 lbs | N/A | N/A | N/A | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | N/A | 1" / 10.3 lbs | N/A | N/A | N/A | N/A | 1" / 12.3 lbs | N/A | N/A
Thickness/Weight per sq. ft. 90 min | N/A | N/A | Nominal 5/16" / 3.0 lbs | 3/4" / 9.0 lbs | N/A | N/A | 1-1/2'' / 12.0 lbs | N/A | 3/16" / 2.5 lbs | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | N/A | N/A | Nominal 1/4" / 3.79 lbs | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | N/A | N/A | 1-7/16" / 17.6 lbs | N/A | N/A | 3/16" / 2.4 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | N/A | N/A | 1-1/2" / 14.6 lbs | N/A | N/A | N/A | N/A | 1-3/16" / 16.4 lbs | N/A
Thickness/Weight per sq. ft. 120 min | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1-1/2'' / 12.0 lbs | N/A | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | N/A | N/A | N/A | N/A | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | N/A | N/A | N/A | 2 -1/4" / 22.9 lbs | N/A | N/A | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | N/A | N/A | N/A | 1-9/16" / 15.8 lbs | N/A | N/A | N/A | N/A | 2-1/8" / 24.6 lbs
Thickness/Weight per sq. ft. 3 hours | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 3/16" / 2.5 lbs | 3/8" / 4.0 lbs | N/A | N/A | N/A | N/A | 3/16" / 2.4 lbs | 5/16" / 4.0 lbs | N/A | N/A | N/A | N/A | N/A | N/A | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/16" / 2.4 lbs | 5/16" / 4.1 lbs | 3/4" / 7.5 lbs | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Max sq. In. 20 min | 3,436 for Aluminum Doors 3,341 for Steel Doors 3,299 for Wood Doors 5,760 for Windows, Sidelites & Transoms Requires AHJ approval for applications other than doors | 3,341 for Steel Doors 5,760 for Steel Windows, Sidelites & Transoms Requires AHJ approval for applications other than doors | 4,608 for Windows & Sidelites 3,456 for Transoms 3,289 for Steel Doors 2,856 for Wood Doors | N/A | N/A | N/A | N/A | N/A | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Doors | 3,204 for Doors Only | 1,296 for Interior Doors Only | 1,296 for Windows, Sidelites & Transoms 3,289 for Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | N/A | N/A | N/A | N/A | 3,419 for Doors Only | 2,736 for Windows, Sidelites & Transoms Only | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Doors | N/A | N/A | N/A | N/A | 3,154 for Steel Windows & Doors Only 2,868 for Wood Doors Only. Requires AHJ Approval for applications other than doors. | N/A | N/A | N/A | N/A
Max sq. In. 45 min | N/A | 5,760 for Steel Windows, Sidelites & Transoms Requires AHJ approval 3,341 for Steel Doors Requires AHJ approval | 4,608 for Windows & Sidelites 3,456 for Transoms 2,856 for Steel Doors 1,296 for Wood Doors | 100 | 4952 | N/A | N/A | N/A | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Doors | N/A | N/A | 1,296 for Windows, Sidelites, Transoms & Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Doors | 4,500 for Windows, Sidelites & Transoms 3,724 for Doors | N/A | N/A | N/A | N/A | 2,736 for Windows, Sidelites & Transoms Only | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Doors | 3,419 for Windows, Sidelites & Transoms 3,419 for Doors | N/A | N/A | N/A | N/A | 4,608 for Windows & Sidelites 2,747 for Doors | N/A | N/A | N/A
Max sq. In. 60 min | N/A | 3,388 for Steel Windows, Sidelites & Transoms (Non-Temperature Rise) Requires AHJ approval 3,341 for Non-Temperature Rise Steel Doors Requires AHJ approval | 960 for Non-Temperature Rise Wood Doors 552 for Non-Temperature Rise Steel Doors 100 for Temperature Rise Doors | 100 | N/A | 4952 | N/A | N/A | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | N/A | 960 for Non-Temperature Rise Wood Doors (when glazed with Pemko FG3000) 100 for Temperature Rise Doors | 3,325 for Windows, Sidelites & Transoms Only | 3,325 for Windows, Sidelites & Transoms 3,204 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,325 for Windows, Sidelites & Transoms 3,204 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | 5,605 for Windows, Sidelites & Transoms 3,724 for Non-Temperature Rise Doors 3,724 for Temperature Rise Doors | N/A | N/A | N/A | 2,736 for Windows, Sidelites & Transoms Only | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,627 for Windows, Sidelites & Transoms 3,627 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | 4,449 for Windows, Sidelites & Transoms 2,685 for Non-Temperature Rise Doors 2,685 for Temperature Rise Doors | N/A | N/A | N/A | N/A | 4,487 for Wall Systems 3,855 for Windows, Sidelites & Transoms 3,855 for Doors | N/A | N/A
Max sq. In. 90 min | N/A | N/A | 552 for Non-Temperature Rise Steel Doors 100 for Temperature Rise Doors | 100 | N/A | N/A | 4876 | N/A | 3,323 For Windows Sidelites & Transoms Only | 3,323 for Windows, Sidelites & Transoms 2,799 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 3,143 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | N/A | 552 for Non-Temperature Rise Doors (when glazed with Pemko FG3000) 100 for Temperature Rise Doors | 2,627 for Windows, Sidelites & Transoms Only | 2,627 for Windows, Sidelites & Transoms 2,034 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,627 for Windows, Sidelites & Transoms 2,034 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | N/A | 3,724 for Windows, Sidelites & Transoms 3,724 for Non-Temperature Rise Doors 3,724 for Temperature Rise Doors | N/A | N/A | 2,736 for Windows, Sidelites & Transoms Only | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 3,534 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | 2,736 for Windows, Sidelites & Transoms 2,736 for Non-Temperature Rise Doors 100 for Temperature Rise Doors | N/A | N/A | 3,174 for Windows, Sidelites & Transoms 3,174 for Non-Temperature Rise Doors 3,174 for Temperature Rise Doors | N/A | N/A | N/A |  | 1,103 for Wall Systems 3,465 for Windows, Sidelites & Transoms 2,196 for Doors | N/A
Max sq. In. 120 min | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4876 | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | 3,724 for Windows, Sidelites & Transoms Only | N/A | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | 4,435 for Windows, Sidelites & Transoms Only | N/A | N/A |  | N/A | 3,828 for Wall Systems Only
Max sq. In. 3 hours | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | N/A | N/A | N/A | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | 100 for Doors Only (Temp. Rise) | N/A | N/A | N/A | N/A | N/A | N/A |  | N/A | N/A
Cost | $ | $ | $ | $ | $$ | $$ | $$ | $$ | $$ | $$$ | $$$$ | $ | $$ | $ | $$ | $$$ | $$$$ | $$$ | $$$ | $$$ | $$$ | $ | $ | $$$ | $$$$ | $$$ | $$$$ | $$$$ | $$$ | $$$ | $$$ | $$$ | $ | $$$ | $$$ | $$$ | $$$
Warranty | Lifetime | Lifetime | 10 years | Lifetime | 5 Years | 5 Years | 5 Years | 5 Years | 10 Years | 10 Years | 5 Years | Unknown | 5 years | 3 years | Unknown | 3 years | 5 years | 5 years | 5 years | 5 years | 5 years | Unknown | Unknown | 3 years | 5 years | 3 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years | 5 years
Applicable IBC Markings | D-20 | D-20/45/60 | D-OH-20/45/60/90 | D-H-45/60/90 | D-T-OH-W-45 | D-T-W-60 | D-T-W-90 | W-120 | OH-20/45/60/90 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-20 | D-20 | D-OH-20/45/60/90 | OH-20/45/60/90 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-T-OH-W-45 | D-T-W-60 | D-T-W-90 | W-120 | D-20 | OH-20/45/60/90 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-OH-20/45/60/90/180 | D-T-OH-W-45 | D-T-W-60 | D-T-W-90 | W-120 | D-20 | D-T-OH-W-45 | D-T-W-60 | D-T-W-90 | W-120
Approved Testing | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, CPSC 16 CFR 1201 Cat. II. This product requires AHJ approval for 45-60 min applications because it does not pass the hose stream portion of the fire test. | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E152, ASTM E163, ASTM E2074, ASTM E2010-01, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, NFRC 100, NFRC 200, NFRC 500, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-2 (1997), UBC 7-4 (1997), NFPA 80, NFPA 257, ASTM E2074-00, ASTM E2010-01, ULC CAN4-S106 | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, ASTM E2010-01, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2, UBC 7-4, NFPA 252, ASTM E2074, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2, UBC 7-4, NFPA 252, ASTM E2074, CSFM 43.7, CPSC 16 CFR 1201 Cat. I | UL 9, UL 10C, UBC 7-2, UBC 7-4, NFPA 252, NFPA 257, ASTM E2074, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 257, CAN4 S-104, CSFM 43.7 | UL 9, UL 10B, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, CAN4 S-104, CAN4 S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 252, NFPA 257, ASTM E2074, CAN4 S-104, CAN4 S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, UBC 43.2, UBC 43.4, UBC 7-2, UBC 7-4, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2074, CAN 4S-101, CAN 4S-104, CAN 4S-106, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 10C, NFPA 80, NFPA 252, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106 | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, CPSC 16 CFR 1201 Cat. II | UL 10B, UL 10C, NFPA 80, NFPA 252, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UL 263, NFPA 80, NFPA 251, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, NFPA 80, NFPA 252, NFPA 257, ASTM E119, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 263, NFPA 251, ASTM E119, ULC CAN4-S101, ULC CAN4-S104, ULC CAN4-S106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10B, UL 10C, UBC 43-2, UBC 7-2 (1997), NFPA 252, ASTM E-152, CSFM 43.7, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-2 (1997), UBC 7-4 (1997), NFPA 252, NFPA 257, ASTM E119, ASTM E2010-99, CAN 4S-105, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UL 263, UBC 7-1 (1997), UBC 7-2 (1997), UBC 7-4 (1997), NFPA 251, NFPA 252, NFPA 257, ASTM E119, ASTM E2010-99, CAN 4S-101, CAN 4S-104, CAN 4S-105, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 9, UL 10C, UBC 7-1 (1997), UBC 7-2 (1997), UBC 7-4 (1997), NFPA 251, NFPA 257, ASTM E119, ASTM E152, ASTM E163, CAN 4S-104, CAN 4S-106, CPSC 16 CFR 1201 Cat. II | UL 263, UBC 7-1 (1997), NFPA 251, ASTM E119, CAN 4S-101, CPSC 16 CFR 1201 Cat. II
Listing Agency | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL & Intertek/Warnock-Hersey Inc. | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL | UL & Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc. | Intertek/Warnock-Hersey Inc.
The information in this document is taken from the manufacturer/distributor’s published information. Please check with the individual manufacturer/distributor for the most up-to-date information.